15A NCAC 18A .2519	FILTERS

(a)  All swimming pools shall be equipped with a filtration system for the purpose of clarifying the swimming pool water; said filtration system shall be an integral part of the circulation system and shall consist of one or more units of sand type filters, of diatomacious earth type filters, or of cartridge type filters.

(b)  All filter units shall be designed and constructed in accordance with Section 5 of the National Sanitation Foundation's Standard number 50 which is hereby adopted by reference in accordance with G.S. 150B-14(c), or equivalent.

(c)  When a sand type filter is installed on a swimming pool, it may be either a gravity or a pressure sand type filter, and it may be either a standard-rate sand type filter which shall be designed for filtration rates not in excess of three gallons per minute per square foot (122 L per minute per square meter) of sand bed area, or a high-rate sand type filter which shall be designed for filtration rates not in excess of 15 gallons per minute per square foot (612 L per minute per square meter) of sand bed area or the flow rate indicated for commercial pools in the most recent NSF listing.

(d)  When a sand type filter is installed on a swimming pool, it shall be designed and installed such that it may be backwashed at a rate recommended by the manufacturer or, in the absence of manufacturer's recommendations, at a rate not less than 15 gallons per minute per square foot (612 L per minute per square meter) of filter bed area. The backwash water shall be discharged to waste. A sight glass or other means for viewing the clarity of the backwash water shall be provided.

(e)  If the sand type filter is designed to be operated in conjunction with a coagulant, a chemical feeder shall be provided for adding the coagulant ahead of the filters.

(f)  When a diatomacious earth type filter is installed on a swimming pool, it may be either a pressure or vacuum type and it may be designed to operate either with or without continuous body feed. Diatomaceous earth filters which operate with continuous body feed shall be designed for filtration rates not in excess of 2.5 gallons per minute per square foot (102 L per minute per square meter) of filter area; and diatomaceous earth filters which operate without continuous body feed shall be designed for filtration rates not in excess of two gallons per minute per square foot (82 L per minute per square meter) of filter area.

(g)  When a diatomaceous earth type filter is installed on a swimming pool, it shall be designed and installed with provisions for cleaning by one or more of the following methods:

(1)	backwashing at two gallons per minute per square foot minimum;

(2)	air-bump-assist backwashing;

(3)	spray wash, (either mechanical or manual); or

(4)	agitation.

(h)  The water used in cleaning a diatomaceous earth type filter shall be discharged to waste, or in a manner approved by the Department.

(i)  When a cartridge type filter is installed on a swimming pool, it shall be designed for filtration rates not in excess of 0.375 gallons per minute per square foot (15 L per minute per square meter) of effective filtration area.

(j)  When a cartridge type filter is installed on a swimming pool, it shall be designed and installed with provisions being provided for cleaning or replacement as recommended by the manufacturer. Two sets of filter cartridges shall be provided to facilitate the cleaning and drying of one set while the filter is operating.

(k)  All filters on swimming pools shall be designed and installed so as to provide easy accessibility for cleaning, operating, maintaining, and servicing. All filter tanks shall be so positioned as to provide adequate circulation of air beneath and around all sides, when necessary, to reduce corrosion and to facilitate cleaning. Whenever filter tanks are installed in the ground (i.e. buried), provisions shall be made so that the tanks are protected against corrosion and are installed in accordance with the recommendations of the manufacturer.

(l)  Filters on swimming pools shall be equipped with an approved type pressure gauge or gauges.

(m)  Filters on swimming pools shall be designed and installed with all the necessary valves and piping which may be needed to drain the filters completely.

(n)  All pressure filters on swimming pools shall be designed and installed with an air-relief valve or valves which shall be located at or near the high point of the filters.

History Note:	Authority G.S. 130A-282;

Eff. May 1, 1991;

Amended Eff. January 1, 1996;

Pursuant to G.S. 150B-21.3A, rule is necessary without substantive public interest Eff. July 20, 2019.